## Slide 1: Enviroway Annual Conference Dragon Slayer for TOC & Chlorine Demand
Kentucky Division of Water
Ken Lake State Park
October 17, 2016

## Slide 2
Filtration Systems are an important part of overall treatment scheme and water quality
Filters are mechanical pieces of equipment
Filtration media is what does the work
Media maintenance can reduce chlorine demand
Operations and Testing can Improve Removal & Reduce Demand
GAC can remove up to 100% of TOC
Reduction in Chlorine means less DBP’s
Take Home Message

## Slide 3
Turbidity
Goal
<1.0 NTU
Turbidity
Goal
<.10 NTU
Achieve
Inactivation
Goal
Finished
Water
Disinfection
Addition
Coagulant
Addition
Variable
Quality
Source
Water
Flocculation/Sedimentation
Barrier
Filtration
Barrier
Disinfection
Barrier
Multiple Barrier Concept for Microbial Contaminant Protection

## Slide 4: Conventional Filtration at Work
CL2 Demand

## Slide 5: Filtration
Filtration removes particles and floc that were not completely settled out during the sedimentation process.
Water passes through materials such as a bed of fine sand, coal, or other granular substance. Particles will be removed through adsorption, absorption, and straining.

## Slide 6: Filtration Has Two Mechanisms
Large particles become lodged and cannot continue downward through media
Mechanical
Adsorption
Particles stick to the media and cannot continue downward through media

## Slide 7: How GAC Works

## Slide 8: Bardstown Water Treatment
Case History

## Slide 9
Bardstown WTP- GAC Trial
PWSID # KY0900017
Treatment Plant Schematic
Bob Cashion, CWT 4-16
WTP Schematic
WTP
1
Actiflo
Sympson
Lake
Reservoir
East #1
West
#2
Clearwell
Clearwell
1
3
4
Filter # 4 GAC Cap Location
HS Pumps
4
2
5
4
4
2
7
6
3
KMNO4
Activated Carbon
Post Actiflo CL2
TOF CL2
Post Filter CL2
PO4
HFS
CL2 Demand

## Slide 10: Raw Water Profile
Daily Test
Best Source to Treat
Manage TOC & Chlorine Demand Issues
Improved Lake Management & Treatment
Improved Pretreatment, Actiflo Treatment and chlorination
Improved Filtration Operations

## Slide 11: Clarification & Filtration in One Unit

## Slide 12: Improvements and Special Studies
Carbon Feed Split
PAC Study
All Carbon is Not the Same

## Slide 13: Improved Chlorine Feed

## Slide 14: Wetted Surface Cleaning
Inorganic & Organic Removal

## Slide 15: Signs and symptoms of filter deterioration
Short filter runs
Lower quality output
High Head Loss
Chlorine Demand
Filters don’t run like they used to….

## Slide 16
Dual Media Filter Assessment
City of Bardstown Utilities
Bardstown Water Treatment Plant
Bardstown, Kentucky 40004
DUAL MEDIA FILTRATION UNITS
June 2015
Bob Cashion, CWT
Business Development Manager
S4 Water Sales and Service, LLC
160 Vanderbilt Court
Bowling Green, KY 42103

## Slide 17
TABLE OF CONTENTS
Executive Summary…………………………………………Preface
Table of Contents 2
Introduction 3
Filter Assessment Sequence 5
Ten State Standard Design……………………………… 6
Filter Valve Integrity Check 8
Filter Backwash Turbidity Profile 9
Floc Retention Analysis 13
Filter Bed Expansion Test (Disc Method) 16
Trough Level and Freeboard 20
Under-drain Inspection 21
Mud-ball, Media Interface, and Media Depth Inspections 22
Surface Wash Inspection/Cleaning 24
Backwash Rise Test 25
Conclusion & Recommendations 26
Appendix………………………………………………… 29

## Slide 18: Filter Units

## Slide 19: Performance Evaluation

## Slide 21
INTERFACE
Sampling Location
Analysis Is Only as Good as Sample

## Slide 22: Is my media Worn out?

## Slide 23: Sieve Analysis Data
Sieve dia. (mm) | Anthracite % Weight Passing | Sand % Weight Passing
2.800 | 99.7 | 100.00
2.000 | 98.34 | 100.00
1.70 | 96.10 | 100.00
1.40 | 83.43 | 100.00
1.00 | 17.87 | 99.81
0.850 | 6.63 | 97.13
0.710 | 0.96 | 80.28
0.500 | 0.96 | 11.19
0.355 | 0.96 | 0.25
0.25 | 0.96 | 0.02

## Slide 24: Sieve Analysis Data
 | Anthracite | Sand
Effective Size (mm) | 0.90 | 0.48
60% Passing (mm) Uniformity Coefficient | 1.26 1.40 | 0.65 1.34

## Slide 25: Floc Retention Analysis
Chart: Bardstown Utilities- WTP Filter 4 Floc Retention Analysis
| 0-2 | 2-6 | 6-12 | 12-18 | 18-24 | 24-30 | 30-36
Before | 5950 | 2490 | 2005 | 1000 | 1840 | 589 | 307
After | 1380 | 1260 | 464 | 551 | 217 | 224 | 185
% Removal | 76.8067 | 49.3976 | 76.8579 | 44.9 | 88.2065 | 61.9694 | 39.7394

## Slide 26: What the Numbers Mean
Floc Retention Test Turbidity (after backwash and rewash) | Bed Cleanliness
10-30 NTU | Very clean, not well ripened
30-60 NTU | Clean and partially ripened
60-120 NTU | Reasonably clean, well ripened
120-300 NTU | Dirty Media, well ripened
300-600 NTU | Dirty Media w/ possible mudballs, well ripened
600-1200 NTU | Very dirty media bed, many mudballs
>1200 NTU | Extremely dirty, chemical cleaning or replacement needed

## Slide 27
Chart: Bardstown Utilities WTP Rate of Rise by Filter
| 1 | 2 | 3 | 4
Standard | 30 | 30 | 30 | 30
 | 15 | 15 | 15 | 15
Rate of Rise (%) | 14.5 | 14 | 15 | 15.4
Expansion Rate of Rise

## Slide 28: Media Cleaning in Lab

## Slide 29
A closer look at an Media Particle – Multiple Layers
1148 Pounds Removed

## Slide 30: Aliquot Sample
Deposits Removed 1148 (lbs.)

## Slide 31: Constituent Clean-Up ANTHRACITE
BEFORE Cleaning
AFTER CLEANING

## Slide 32: Constituent Clean-Up SAND
BEFORE Cleaning
AFTER CLEANING

## Slide 33: Constituent LOADING

## Slide 34: Constituent LOADING
6010 MET ICP
Analytical Method: EPA 6010 Preparation Method: EPA3010
Parameters ICP Results Units Report Limit Wt. %
PARAMETERS | RESULTS | UNITS | REPORT LIMIT |  | WT%
Aluminum | 2100 | Mg/l | 0.075 |  | 71.3 %
Calcium | 364 | Mg/l | 0.1 |  | 12.4 %
Manganese | 77.6 | Mg/l | 0.005 |  | 2.6 %
Phosphorus | 136.8 | Mg/l | 0.1 |  | 4.6 %
Silicon | 139.0 | Mg/l | 0.5 |  | 4.7 %
 |  |  | Total |  | 100.0%

## Slide 35: Pre Cleaning Cl2 Data
Free | Total | Difference
1.8 | 3.16 | 1.36
1.54 | 3.02 | 1.48
1.69 | 3.06 | 1.37
1.53 | 2.86 | 1.33
1.8 | 3 | 1.2
1.73 | 2.72 | 0.99
1.7 | 2.9 | 1.2
1.57 | 3.12 | 1.55
1.66 | 3.08 | 1.42
1.3 | 2.72 | 1.42
1.61 | 2.92 | 1.31
1.53 | 3.2 | 1.67
1.75 | 3.3 | 1.55
1.66 | 3.14 | 1.48
1.41 | 2.92 | 1.51

## Slide 36: Chlorine Demand
Plant Free | Plant Total | Difference
1.17 | 1.47 | 0.3
1.13 | 1.37 | 0.24
0.98 | 1.26 | 0.28
1.08 | 1.31 | 0.23
1.18 | 1.41 | 0.23
1.31 | 1.44 | 0.13
1.1 | 1.34 | 0.24
1.12 | 1.53 | 0.41
1.32 | 1.51 | 0.19
1.15 | 1.49 | 0.34
1.07 | 1.34 | 0.27
1.26 | 1.53 | 0.27
1.49 | 1.69 | 0.2
1.57 | 1.8 | 0.23
1.28 | 1.52 | 0.24
1.14 | 1.48 | 0.34
July 2015

## Slide 37: Chlorine Demand
Free | Total | Difference
1.33 | 1.58 | 0.25
1.4 | 1.64 | 0.24
1.23 | 1.48 | 0.25
1.19 | 1.43 | 0.24
1.22 | 1.47 | 0.25
1.23 | 1.49 | 0.26
1.19 | 1.43 | 0.24
1.24 | 1.38 | 0.14
1.09 | 1.33 | 0.24
1.41 | 1.72 | 0.31
1.14 | 1.38 | 0.24
1.05 | 1.31 | 0.26
1.03 | 1.23 | 0.2
1.1 | 1.31 | 0.21
1.04 | 1.36 | 0.32
1.44 | 1.82 | 0.38
August 2015

## Slide 38: Benefits of Cleaning Process
Less Chlorine Feed
Improved Filtration
Less Backwash Water
Longer Filter Runs
Esthetic Quality
Improved Water Quality

## Slide 39: State of Kentucky Approval
First Split GAC Cap Approved in KY- June 24, 2016
Stipulation Based on previous Engineering Specification
2-4 GPM/Square Foot Contact time 528 Square feet with 48 inches GAC- 900 Iodine Number- 10” Sand
Backwash Flow Rate Issue
No TOF Chlorine Feed
HPC bottom of filter control mechanism
Biological Filtration Operation

## Slide 40
48” GAC
10” Sand
Filter Media Depths
Bardstown WTP GAC Project
PWSID # KY0900017
Filters # 4 “ As Built GAC Cap”
Bob Cashion, CWT 7-22-16
“As Built GAC Cap” Filter # 4
AWI Underdrain
Sand Elev. 468.33
GAC Elev. 472.33
Weir Elev. 476.25
AWI Elev. 467.50
50% Expansion
Elev. 474.75
AWI Underdrain
Plenum
Wall Elev. 483.75
Bottom Elev. 464.50
4.833’ of Total Media
33.125” Free-board at Rest
476.25
6800 gpm BW rate gave 7” Rise Rate @ 12%

## Slide 41: Anthracite Media Removed to Sand Level

## Slide 42: Bardstown GAC Installation

## Slide 43: Sand & GAC skimming

## Slide 44
48” GAC
10” Sand
Filter Media Depths
Bardstown WTP GAC Project
PWSID # KY0900017
Filters # 4 As Built Drawing
Bob Cashion, CWT 7-16
“As Built GAC Cap” Filter # 4
AWI Underdrain
Sand Elev. 468.33
GAC Elev. 472.33
Weir Elev. 476.25
AWI Elev. 467.50
50% Expansion
Elev. 474.75
AWI Underdrain
Plenum
Wall Elev. 483.75
Bottom Elev. 464.50
Expansion Elev. 472.91
12 % Expansion at 6800 gpm

## Slide 45: Unit # 4 TOC Levels Before & After
Mg/l as Total Organic Carbon- Inline TOC Monitor
Average before Toc Removal Through Dual Media Filtration TOF Verse BOF 17.32%
Average After Gac Installation through Cap Bed Filtration 91.79% Removal
Current Average 95-100 % removal

## Slide 46: DPB Data
Lowest 3rd Quarter (Aug-16) numbers in History of the facility
Plant Tap-Haa5- 0.024 ttHM-0.035
N Neson-0.019 0.031
Bloomfield 0.028 0.038
New haven- 0.05 0.058
MCL@ 60ppb MCL @ 80ppb

## Slide 47: Summary
  More importance is being place on filtration.
  Media is What Does the Work
  Yearly Inspection & Assessments are necessary.
  Media cleaning is less expensive than complete replacement.
  New technology can put your mind at ease.
  GAC is here to stay
  Improved chlorine demand, more efficient filtration.
  Cleaning is a good thing!

## Slide 48
For further information:
Bob Cashion, Business Development Manager
T: 270-790-2726
rkcashion@s4water.net
The information included in this presentation is proprietary and/or confidential, and protected from disclosure. Do not disseminate, distribute or copy this presentation without the express consent of S4 Water Sales & Service, LLC