## Slide 1: Development of a Filter Surveillance Program Part 2
Brandt Cashion
S4 Water Sales and Service, LLC

## Slide 2: Filter Bed/Media Tests
Top of Gravel Footprint
Filter Coring/Sampling
Media Inspections
Filter Excavations
Notes: Fig 10

## Slide 3: Top of Gravel Footprint Testing
Gravel helps
Evenly distribute backwash water
Gives support to finer media
Purpose: To ascertain the levelness of the gravel layer
Importance: Can result in uneven backwash water distribution, poor media statification

## Slide 5: Top of Gravel Footprint Testing

## Slide 6: Top of Gravel Footprint Testing

## Slide 7: Top of Gravel Footprint Testing

## Slide 8: Top of Gravel Footprint Testing

## Slide 9: Media – Surface Profiles
Measured down from trough to media
Use a 5’ level to check the media surface

## Slide 10: Freeboard Elevation Footprint Testing

## Slide 11: Top of Gravel Depth of Media Testing
32 in. | 30 in. | 29 in. | 28 in. | 27 in. | 26 in.
29 in. | 29 in. | 29 in. | 27 in. | 27 in. | 26 in.
29 in. | 28 in. | 26 in. | 27 in. | 27 in. | 27 in.
29 in. | 29 in. | 26 in. | 26 in. | 27 in. | 27 in.
29 in. | 29 in. | 29 in. | 28 in. | 27 in. | 27 in.
28 in.
27 in.
28 in.
28 in
28 in
29 in
29in. 29 in. 29 in. 29 in. 27 in. 28 in

## Slide 12: Media Depth

## Slide 13: Filter Coring
Purpose:
To sample media throughout the depth of the bed
Importance:
Allows you to obtain samples that can be used in sieve analysis and floc retention profile testing

## Slide 14: Filter Coring Steps

## Slide 15: Filter Coring

## Slide 16: Filter Coring

## Slide 17: Filter Coring

## Slide 18: Filter Coring
Anthracite
0-12”
Transition 12”-18”
Sand Layer 18”-24”

## Slide 19: Media Inspections
Purpose: To determine the state and condition of the media
Importance: Media state and condition affects filter performance
Notes: Fig 10

## Slide 20: Media Inspections-Filter Mounding
Mounding may be caused by the gravel layer being disturbed allowing more backwash through at that point.
Notes: Fig 10

## Slide 21: Media Inspections-Mudball Formation
Mudballs can form over time because of improper or inefficient backwashing
Notes: Fig 10

## Slide 22: Mud Balls

## Slide 23: Microscopic Media Evaluations
Anthracite
Sand
Untreated
Treated

## Slide 24: Media Analysis

## Slide 25: Media Analysis

## Slide 26: Questions?