## Slide 1
Basic boiler and boiler water training

## Slide 2: Objectives of Boiler Water Treatment
Prevent Scale and other Deposits in Pre-Boiler, Boiler and Condensate Systems.
Prevent Corrosion in Pre-Boiler, Boiler, Steam, and Condensate Systems.
Provide Required Steam Purity.

## Slide 3: Effects of Poor Boiler Water Treatment
Operational Upsets & Unscheduled Outages.
Reduced Plant Safety & environmental/regulatory Non-compliance
Excessive Costs
Limited Reliability

## Slide 4: Basic steam generation cycle
2 Boiler
1 Pre-Boiler
4 Condensate
3 Steam

## Slide 5: Boiler sub-systems
Pre-boiler: Feed water piping, Feed water heaters, and deaerator.
Boiler
Steam
Condensate

## Slide 6: pretreatment system components
Softeners
Reverse Osmosis Units
Demineralizers
Dealkalizers
Combinations of above

## Slide 7: Why do we care about feed water contaminate levels?
Deposition is the primary driver

## Slide 8: solubility vs temperature
Temperature
Ion
Concentration
In Solution
Calcium/
Magnesium
Concentration
In Solution
Regular
Retrograde

## Slide 9
Steam-sparge of feedwater tank
Example of a Feedwater tank

## Slide 10
CHARLES’ LAW
  OXYGEN SOLUBILITY DECREASES WITH INCREASING WATER TEMPERATURE
TEMPERATURE, F
22.9 ppm
20.0
17.2
14.3
11.4
8.6
5.7
2.9
0.0
TEMPERATURE, C
0 50 70 90 110 130 150 170 190 210 230 250
cm3/l 16
14
12
10
8
6
4
2
0 10 21 32 43 54 66 77 88 99 110 121
DEAERATOR GAUGE PRESSURE POUNDS
10
8
6
4
2
0
4
8
12
16
20
24
28
VACUUM INCHES
MERCURY
Atmospheric
Pressure
(0 psig)
O2 Solubility in water
Notes: The solubility of oxygen in water is dependent upon the temperature and pressure.
Oxygen content of cold makeup (70 F) will contain 8 to 10 ppm of oxygen.
The incoming stream of water to the Deaerator is sprayed into fine droplets or spilled over trays to maximize the waters steam contact .
2. Fresh steam is added so it can have intimate contact with the water. This heats the water to that of the saturated steam temperature.
3. The heating of the water drives the non-condensable gases (such as oxygen) off into the vapor phase.
4. Venting of these hot gases/steam from the deaerators producers an extremely low O2 gas environment.
5. This in turn results in oxygen values of less than 7 ppb in feedwater.

## Slide 11: Type of deaerator
TO FEEDWATER PUMP
MIXING TEE
CONDENSATE
HEATER TANK
COLLECTOR
STEAM EQUALIZER
DOWNCOMER
STORAGE TANK
MAKEUP
VENTS
VALVES, NOZZLES
STEAM
BAFFLES
COUNTER-CURRENT
UPWARD FLOW
SCRUBBER SECTION
Spray Type
Notes: Spray Scrubbing Deaerators
Perform best at stable high load conditions.
Perform best when approaching water stream is approximately 50 0 F less than the feedwater temp. (Higher temperatures reduce the amount of steam addition and can lead to increased venting needs).
Rely on excellent spray nozzle operation to break the water up into fine droplets.

## Slide 12
Venting the DA is critical

## Slide 13: poor mechanical deaeration

## Slide 14: dissolved oxygen
Mechanically removed in deaerator to < 7 ppb guarantee. Typical performance 20-50 ppb.
Chemically lowered to <10 ppb.
Dissolved oxygen causes corrosion in Preboiler, Boiler, Steam, and Condensate Systems.
#1 cause of failure in low-pressure boilers.

## Slide 15: chemical scavenging
Sulfites/bi-Sulfites are utilized to reduce the remaining oxygen in the feedwater.
Direct reaction with sulfite generates sulfate.
Operators measure residual sulfite.
Good scavenger performance depends upon
  Time, temp, pH, and catalyst level

## Slide 16: sodium bisulfite
Best conditions for maximum performance.
  pH > 8.5
  Time > 10 minutes
  Temperature > 230 F
  Catalyst present

## Slide 17: types of Boiler systems
Firetube ~
Watertube ~
Waste heat ~ waste heat is used to make steam
HRSG ~ Heat Recovery steam generator

## Slide 18: ASME (American Society of Mechanical engineers) Guidelines
Based upon what has worked industrially for years in standard boilers which are:
  Industrial water tube with or without superheaters and turbine drives
  Industrial firetube boilers
  Coil boilers
  Marine boilers
  Electrode boilers

## Slide 19
Dissolved Oxygen
Iron, Copper, Hardness, and Suspended Solids
pH
Organic Matter
Silica
Alkalinity
Conductivity
ASME water parameters to monitor

## Slide 20: asme water chemistry guidelines

## Slide 21
Scale Thickness (Inches)
Energy Loss (%)
Iron & Silica
High Iron Content
"Normal" Scale
0
1
2
3
4
5
6
7
8
1/64
1/32
3/64
1/16
Energy loss vs scale thickness

## Slide 22
600 F
o
500 F
o
Metal
Wall
Tube
Waterside
Fireside
Without Scale
800 F
o
500 F
o
Metal
Wall
Tube
Waterside
Fireside
Scale
With Scale
boiler tube heat transfer

## Slide 23: pH
pH between 8.3 - 10.5 for Feed water will minimize corrosion.
pH between 9.5 - 12.5 in Boiler will minimize corrosion.
Low pH in Condensate system caused by carbonic acid - Carbon Dioxide in condensate system.

## Slide 24: pH
M or Total Alkalinity = pH is 4.3 and above
Acidic
Basic
Hydrogen Ions Increase
pH
1
2
4
5
6
7
8
9
10
11
12
13
14
3
OH alkalinity = ph of 10.2 and above
P alkalinity = pH of 8.2 and above

## Slide 25
  Minimize deposition
  Minimize corrosion
  Minimize carryover
objectives of internal treatment
  By meeting these goals we maximize your equipment reliability and minimize your cost of operation.
  Your pretreatment equipment is the front line of defense.

## Slide 26
How?
maximizing efficiency
By maximizing condensate return
Return on effort
        High energy value
        Good quality water
        Lowers overall water costs
        Lowers chemical treatment cost
        It’s not free

## Slide 27
Carbon Dioxide occurs in the atmosphere and can leak into the steam system.
Carbonate and Bicarbonate Alkalinity break down under thermal conditions and produce Carbon Dioxide.
Carbon Dioxide forms Carbonic Acid, a weak acid, and lowers the pH of the condensate system.
Condensate corrosion

## Slide 28
+
CO2
Carbon
Dioxide
H2O
Water
H2CO3
Carbonic Acid
Steam Phase
Condensate Phase
Carbonic acid formation

## Slide 29
Pretreatment approaches
  RO
  Softener
  Demin
Chemical treatment approaches
Condensate polishing
How to protect the condensate system

## Slide 30
Neutralizing amines
Chemical approach
filming amines

## Slide 31
Chemical approach
  Work on the basis of a weak organic base neutralizing the carbonic acid.
  Are highly effective and easy to feed and control
  Provide no protection against oxygen
  FDA approved products available
  Can improve oxygen scavenger performance
  Higher alkaline waters require more product.

## Slide 32
DR vs. Pressure
AMINE 0 PSIG 200 PSIG 1000 PSIG
CYCLOHEXYLAMINE 4.0 16.0 9.3
DEAE 1.7 4.5 3.4
MORPHOLINE 0.4 1.6 1.0
3 common amines
Notes: DEAE – Diethylethanolamine
MOPA – Methoxypropylamine
MEA – Monoethanolamine

## Slide 33
METAL SURFACE
Hydrophobic Barrier Film
HYDROPHILIC
ANCHOR
Filming amines
Notes: Review Of Filmer Technology
The picture effectively illustrates how a filmer functions to protect the metal surface. The film does not impede heat transfer; in fact, it may enhance it by promoting drop wise condensation (vs. film condensation).
The integrity and stability of the mono-molecular film is key to performance.

## Slide 34
METAL SURFACE
Hydrophobic Barrier Film
O2
H2CO3
How it protects
Notes: Review Of Filmer Technology
A properly applied filmer program will protect metal surfaces from corrosion. This concept is similar to what you do when you apply wax to the metal surface of your car - protecting the surface from the weather.
It can be noted that the film protection is not perfect, e.g. the filming process is dynamic with film continuously being stripped away and again replenished. As a result, the metal will be exposed somewhat to the corrosive environment.
Note, the filmer itself does nothing to change or modify the corrosive liquid.

## Slide 35: Carryover
Refers to any contamination that leaves the boiler with the steam.
The most common carryover is entrained boiler water droplets which contain dissolved and suspended solids.
Carryover may be either mechanical or chemical.
Types of carryover include spray carryover, priming, and foaming.
Common concerns & terms

## Slide 36: Organic Matter
Consists of Oily Matter & Non-volatile Total Organic Carbon.
Organic contamination can cause internal deposition and/or boiler carryover.
Oily Matter includes hydrocarbons, vegetable oils, animal fats, waxes, soaps, and greases. Limit < 1 ppm in Feedwater.
TOC < 1 ppm in Feedwater.
Common concerns & terms

## Slide 37: Silica
Responsible for internal deposition of complex silicates.
Silica scale more retardant to heat transfer.
Limit < 150 ppm in Boiler Water.
Silica in higher pressure systems is volatile and can affect downstream equipment via deposition.
Common concerns & terms

## Slide 38: Alkalinity
P Alkalinity = 1/2 carbonates and all hydroxides.
M Alkalinity = Total Alkalinity = All bicarbonates, carbonates, and hydroxides.
O Alkalinity = All hydroxides.
Alkalinity affects pH, deposition, sludge conditioning, and steam purity.
Common concerns & terms

## Slide 39: Conductivity
Corresponds to the level of Total Dissolved Solids in the Boiler.
Used for blowdown control to limit cycles of concentration.
Exceeding conductivity guidelines can result in carryover.
Common concerns & terms

## Slide 40: Any Questions?
?