## Slide 1: Lessons Learned: Fighting DBP Formations for improved water quality
KRWA 39th Annual Conference & Exhibition
Louisville, Kentucky
August 27- 28, 2018

## Slide 2: Take Home Message
History can be beneficial- Peer Review/ State of Commonwealth
Never Before Have there been so many options to remove organics
Implementation of Solutions in a systematic approach Improves Success of Problem Solving.
you can Never can have to much data
water Systems are Dynamic
Options do not stop at the Treatment Plant
Optimization and Management of Source water ,treatment & Distribution system improves water quality

## Slide 3: The State of the Commonwealth
Current Regulations & Compliance in Kentucky
Stage 1 & 2 (11 DPB’s) Since 2015
Total Water Systems- 435 Public Water Systems
Non Compliant Systems-44
Consecutive Systems- 29
Trending Down

## Slide 4: Violation Trends

## Slide 6: Violations
Chart: Surface Water and Surface Water Purchaser Violations Per Analyte Name
| SW/2017 MCL TTHM | SW/2017 MCL HAA | SWP/2017 MCL TTHM | SWP/2017 MCL HAA | GWP/2017 MCL HAA | SW/2016 MCL TTHM | SW/2016 MCL HAA(5) | SWP/2016 MCL TTHM | SWP/2016 MCL HAA(5) | SW/2015 MCL TTHM | SW/2015 MCL HAA(5) | SWP/2015 MCL TTHM | SWP/2015 MCL HAA(5) | SW/2014 MCL TTHM | SW/2014 MCL HAA(5) | SWP/2014 MCL TTHM | SWP/2014 MCL HAA(5)
Total Number of Water Systems | 15 | 10 | 18 | 29 | 2 | 14 | 20 | 27 | 33 | 9 | 13 | 30 | 46 | 12 | 7 | 20 | 12

## Slide 7: Stage 2
Disinfectant And Disinfection Byproduct Rule (DBPR USEPA 2015)
4- THMs
5-HAAs
Chlorites
Bromates
Precursor Removal

## Slide 8: Control Strategies
Three Primary Categories:
Removal of DBP Precursors (TOCs)
Modification and optimization of treatment and disinfection practices to minimize DBP formation
Removal of dbp’s after formation

## Slide 9: Treatment Applications
Pre-Oxidation
Oxidation & Aeration
Feed Points
Adsorption with Pac
Enhanced Coagulation
Alternate disinfection methods
Filtration with Gac

## Slide 10: TTHMs & HAAs
After Reaction Formation- Best Methodology
Formed by reaction with NOM and chemical disinfectant
Reducing NOM- Watershed Management
Removing Pre-Chlorination
Enhanced Coagulation
GAC
Ultra or Nano Filtration
Biological Filtration
All Carbon is Not the Same

## Slide 11
48” GAC
10” Sand
Filter Media Depths
Bardstown WTP GAC Project
PWSID # KY0900017
Filters # 4 “ As Built GAC Cap”
Bob Cashion, CWT 7-22-16
“As Built GAC Cap” Filter # 4
AWI Underdrain
Sand Elev. 468.33
GAC Elev. 472.33
Weir Elev. 476.25
AWI Elev. 467.50
50% Expansion
Elev. 474.75
AWI Underdrain
Plenum
Wall Elev. 483.75
Bottom Elev. 464.50
4.833’ of Total Media
33.125” Free-board at Rest
476.25
6800 gpm BW rate gave 7” Rise Rate @ 12%

## Slide 12
Some Typical Stripping Towers

## Slide 13
Treatment Plant Schematic
Bob Cashion, CWT 4-17
WTP Schematic
Filter units
Actiflo
35 Acre City
Reservoir
1
HS Pumps
2
4
7
6
3
KMNO4
Activated Carbon
Post Actiflo CL2
TOF CL2
Post Filter CL2
PO4
HFS
Actiflo
500K
300 K

## Slide 14: Alternative Feed Points
Critical for Success
What Mechanism ?
Feed Rate
Demand
Residual
Monitoring Points
Water Quality Changes

## Slide 15: Filtration Works
Enhanced Coagulation
pH depression to break DOC Bond
or
Enhanced Softening

## Slide 16
Turbidity
Goal
<1.0 NTU
Turbidity
Goal
<.10 NTU
Achieve
Inactivation
Goal
Finished
Water
Disinfection
Addition
Coagulant
Addition
Variable
Quality
Source
Water
Flocculation/Sedimentation
Barrier
Filtration
Barrier
Disinfection
Barrier
Multiple Barrier Concept for Microbial Contaminant Protection
Bio Filtration or GAC Contact Time

## Slide 17: Filtration Has Two Mechanisms
Large particles become lodged and cannot continue downward through media
Mechanical
Adsorption
Particles stick to the media and cannot continue downward through media

## Slide 18: Contact Time = Removal Results

## Slide 19: Benefits of Activated Carbon
Taste & Odor MIB/ Geosmin
Cyano Toxins
TOC
DPB’s and Precursors
Endocrine Disruptors
Pharmaceuticals

## Slide 20: Causes of DBP Accumulation
1. Poor source water quality
2. Inadequate water treatment/
filter media fouling
3. Contamination and long residence time in the storage and distribution system
Purchasing Systems/ Consecutive Systems

## Slide 21: Objectives Chart
TOC Reduction Fight Low Chlorine Residual
SOLUTIONS
Residence Time
DEMAND
Flushing
Tank Turn Over
Chemical Feed
Training

## Slide 22: Remediation Critical Control Points
Wetted Surface cleaning
Aeration
Storage Tank
cleaning
Source Water Protection, Raw Water Line & Storage cleaning
Filtration Media cleaning
Reduction of chlorine feed, Distribution Line cleaning
Water Contact Time
Wetted Surfaces
4-6 Hrs.
24-96 Hrs. +
Pre Oxidants
Notes: Blue Earth Labs’ Cleaning Mechanisms- Source to Tap. NSF approved Off line & On Line Cleaning chemistries and products for each portion of the infrastructure.

## Slide 23: Distribution Applications
Main Flushing
Storage Management
Water mixing
Main Cleaning
Biofilm Removal & Prevention
Elimination of Dead Ends
Satellite Feed Systems
Filtration

## Slide 24: What Contributes to Water Age?
Long Residence time in storage tanks
Fire Flow requirements in new construction Area
Low flow & Lack of Water usage in large diameter piping
Dead end lines with low usage
High Chlorine Demand (Organic & Inorganics)

## Slide 25: “Issues with Water Age”
Chemical Biological Physical
*DBP Formation *Biodegradation Temp Increase
Disinfection Decay *Nitrification Sediment
*Corrosion Control *Microbial Regrowth Color
Taste & Odor Taste & Odor Smell
*Potential Health Impacts associated with chemical and biological issues

## Slide 26: Technical Briefing
Water Age – Increases formation of contaminates in tanks, pipes, pipe walls & bulk water that can lead to adverse health effects.
Distribution System is a Reactor That
Affects Water Quality
Water Quality Problems: Dbp’s,
Nitrification, Microbial Survival & Growth and Corrosion
Residence Time, System Turnover

## Slide 27: Distribution System Treatment
GAC Filter Prior to Re-chloramination

## Slide 28: Sampling & Laboratory Management
Represenative Water Samples
Preliminary & Surrogate Testing
Split Samples Verification
Check Lab Results, Temperature, Holding Times

## Slide 29: System Wide Bacteria Testing
BART’s Test Utilized to provide bacteria colony counts leaving the WTP and through out the distribution System. Slime, Iron & Sulfur Reducing Bacteria
Slime and Iron Bacteria Positive

## Slide 31: Organics + Chlorine= DBP’s
Chlorine Residual
DBPs

## Slide 32: Water Storage

## Slide 33: Distribution Monitoring
Loss of Disinfectant Residual
Increase in water temperature
Decrease in pH(Lower alkalinity affects buffering capability)
Decrease in Alkalinity(Significant amount of Bicarbonate consumed during nitrification)
Decrease in dissolved oxygen
Increase HPC (Heterotrophic Plate Count)
Bacterial re-growth

## Slide 34: What’s next
Bacteriological sampling/bio penetrant feed
Pressure zone specific fluoride tracer study
Implement changes to valving (open/close) to prevent sloshing
Work with purchasers (wD) to continue water age study in their systems
Once changes are implemented, dbp testing, bacteriological sampling

## Slide 35: Case Study Central City WTP
PAC Study-Highest Iodine number
Tracer Study-
Bacteria Study-
Phosphate Study
Main Flushing-
Tank Management-

## Slide 36: Case Study Bardstown WTP
Lowest 3rd Quarter (Aug-16) numbers in History of the facility
WTPHaa5- 0.024 ttHM-0.035
N Neson-0.019 0.031
Bloomfield 0.028 0.038
New haven- 0.05 0.058
MCL@ 60ppb MCL @ 80ppb

## Slide 37: Case Study Lebanon WTP
OPTIMIZATION
Water Source Quality
Pre-oxidant Testing
Chemical Feed Points
Carbon Selection
Filtration Performance
Clearwell Management
Unidirectional Flushing of System
Tank Storage Management
Improved Sampling Plan
Background and Non Compliant Testing
Training

## Slide 38: QUESTIONS???????
" It's not what you know, it's knowing where to find what you need. "
Contact information:
Bob Cashion 270-790-2726
RKCashion @S4Water.net
The information included in this presentation is proprietary and/or confidential, and protected from disclosure. Do not disseminate, distribute or copy this presentation without the express consent of S4 Water Sales & Service ,LLC